**Atkore – FRE® Composites**

This product specification is written according to the Construction Specifications Institute

*MasterFormat,* 2018 Update.

**SECTION 26 05 33.13**

**CONDUIT FOR ELECTRICAL SYSTEMS – Epoxy Reinforced Thermosetting Resin Conduit (“RTRC”)**

# PART 1 - GENERAL

* 1. RELATED DOCUMENTS
		1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections apply to this Section.

# DEFINITIONS

* + 1. RTRC: Reinforced Thermosetting Resin Conduit-Epoxy

# SUMMARY

* + 1. This Section includes the following:
		2. Reinforced Thermosetting Resin Conduit (“RTRC”)
		3. Related Sections
			1. Section 26 05 26 “Grounding and Bonding for Electrical Systems”
			2. Section 26 05 29 “Hangers and Supports for Electrical Systems”
			3. Section 26 05 33.16 “Boxes for Electrical Systems”
			4. Section 27 05 33 “Conduits and Backboxes for Communications Systems”
			5. Section 25 05 28.33 “Conduits and Backboxes for Integrated Automation”

# REFERENCES

* + 1. UL 2515 Safety Standard - Aboveground Reinforced Thermosetting Resin Conduit and Fittings.
		2. UL 2515A Safety Standard - Supplemental Requirements for Extra Heavy Wall Reinforced Thermosetting Resin Conduit (RTRC) and Fittings.
		3. NFPA 70 NEC 501.10(B) Class 1 Division 2(1)(6)
		4. CSA C22.2 NO. 2515:19 Aboveground Reinforced Thermosetting Resin Conduit (RTRC) and fittings-For type SW only (Binational standard with UL 2515).
		5. CSA: C22.2 No. 2515.1-13 Supplemental requirements for extra heavy wall (XW) Reinforced Thermosetting Resin Conduit (RTRC) and Fittings.
		6. UL 2420 Safety Standard - Belowground Reinforced Thermosetting Resin Conduit (RTRC) and Fittings.
		7. CSA C22.2 No. 2420-09 Belowground Reinforced Thermosetting Resin Conduit (RTRC) And Fittings (Bi-National Standard, with UL 2420).
		8. NEMA TC-14.AG, NEMA TC-14. XW and NEMA TC-14.BG Standards for Reinforced Thermosetting Resin Conduit (“RTRC”). Note: These are NEMA Adoptive Standards: NEMA TC-14.AG (UL 2515), NEMA TC-14. XW (UL 2515A) & NEMA TC-14.BG (UL 2420)
		9. CSA C22.1:21 Canadian Electrical Code, Part I, Safety Standard for Electrical Installations
		10. NECA National Electrical Installation Standard (NEIS) 111, Standard for Installing Nonmetallic Raceways.

# SUBMITTALS

* + 1. Manufacturer’s Product Data
		2. Certifications to applicable standards
		3. Domestic certifications where required to applicable standards.

# QUALITY ASSURANCE

* + 1. Reinforced Thermosetting Resin Conduit and Fittings complies with one of the following UL Listings; UL 2420, UL 2515, UL2515A.
		2. Reinforced Thermosetting Resin Conduit and Fittings are CSA Listed and manufactured in accordance with CSA C22.2 NO. 2515:19, CSA: C22.2 No. 2515.1-13 and CSA C22.2 No. 2420-09
		3. Reinforced Thermosetting Resin Conduit conforms to NFPA 70 (NEC 2020 Article 355).
		4. Reinforced Thermosetting Resin Conduit conforms to Canadian Electrical Code (CEC Article 12-200).
		5. Electrical equipment and materials shall be new and complying with the latest codes and standards. No used, re-built, refurbished and/or re- manufactured electrical equipment and materials shall be furnished on this project.
		6. Testing Agency Qualifications: Testing/listing agency shall be one of the following Nationally Recognized Testing Laboratories:
			1. Underwriters Laboratories (UL)
			2. Canadian Standards Association (CSA)

# STORAGE AND HANDLING

* + 1. Storage: Whenever possible, store the conduit indoors to prevent possible discoloration, the accumulation of dirt and to extend the life of the product. If conduit is stored outdoors, it should be in a shaded area to avoid as much as possible UV exposure. It shall be stored in such a way as to allow air circulation and water drain-off and shall not be directly covered with plastic.
		2. Conduits are shipped in self-supporting crates designed to be unloaded by forklift. Crates should not be dropped from the truck trailer flat beds. Each crate shall be legibly marked with the following information:
1. Manufacturer's identification
2. Product description
3. Stock number
	* 1. All Type SW, HW and XW Conduits, elbows and fittings shall be durably and legibly marked in accordance with the standard UL Listing. In addition, the following information shall be included in the marking:
4. Manufacturer
5. The Application and Applicable UL Standard: UL 2515, UL 2515A (for type XW only) and UL 2420
6. The CSA Logo (in Canada)
7. The wording “Reinforced Thermosetting Resin Conduit and Fittings”
8. Part Number, Description and Trade Size
9. Operating Temperature
10. Wall Thickness
11. Elbows are Marked with the Angle and Radius
12. Date of Manufacturing of Conduit, Elbows, and Fittings
13. Country of Origin
	* 1. Conduit crates should be stored on a level surface in an environment free from excessive dirt, dust, or other airborne contaminants. The vertical support of the wooden frames should line up so the load will be transferred to the wood frames rather than the conduit. The height of stacked conduit should be limited to twelve feet.
		2. Packing system for conduits and fittings shall be provided with adequate amount of interval support spacing during shipping and subsequent storage by the customer to mitigate any deflection or deformity.
		3. Elbows and accessories, when stored outdoors, it should be in a shaded area to avoid as much as possible UV exposure amongst other elements.
		4. A two-part adhesive kit will have a minimum shelf life of 12 months from delivery date when stored per the manufacturer's recommendations. The manufacturing date should be printed on the cartridge's label. Storage and handling should comply with Manufacturer’s storage and handling guidelines.

# PART 2 – PRODUCTS

* 1. MANUFACTURERS
		1. Atkore – FRE® Composites (BAA – BABA)

60 Greenhorn Drive

Pueblo, CO 81004

* + 1. Atkore – FRE® Composites

75 Wales

Saint-Andre’-d ’Argenteuil QC JOV1X0

Canada

* 1. REINFORCED THERMOSETTING RESIN CONDUIT-EPOXY
		1. Basis-of-Design Product: Subject to compliance with requirements, provide Atkore FRE® Composites (RTRC) fiberglass conduit.
		2. RTRC Epoxy Conduit Type SW, HW and XW is available in trade sizes ¾ up to 8” IPS and 2” up to 6” ID trade sizes.
		3. RTRC Epoxy Conduit nominal conduit wall thicknesses as basis-of-design
		4. RTRC Conduit Type SW Wall Thickness: ¾” -1-1/2” (IPS - .066”)
		5. RTRC Conduit Type SW Wall Thickness: 2” - 4” (IPS - .070”), 2”-4” (ID - .070”)
		6. RTRC Conduit Type SW Wall Thickness: 4-1/2” (ID - .095”)
		7. RTRC Conduit Type SW Wall Thickness: 5” (IPS - .095”), (ID - .095”)
		8. RTRC Conduit Type SW Wall Thickness: 6” (IPS - .110”), (ID - .095”)
		9. RTRC Conduit Type SW Wall Thickness: 8” (IPS - .115”)
		10. RTRC Conduit Type HW Wall Thickness: 4” (IPS - .095”), (ID - .095”)
		11. RTRC Conduit Type HW Wall Thickness: 5” – 6” (IPS - .115”), (ID - .115”)
		12. RTRC Conduit Type XW Wall Thickness: 3’4” – 8” (IPS - .250” - .250”), (ID - .250” - .250”)
		13. RTRC Conduit Glass Content minimum (SW 68% ± 3%), (HW 68% ± 3%), (XW 71% ± 3%) per API 15LR
		14. RTRC Conduit is listed to UL 2420, UL 2515, or UL 2515A.
		15. RTRC Conduit is listed to CSA and manufactured in accordance with CSA C22.2 NO. 2515:19, CSA: C22.2 No. 2515.1-13 and CSA C22.2 No. 2420-09.
			1. Thin Wall (TW) for Encased Buried (EB) installations only
			2. Standard Wall (SW) for Encased Buried (EB) or Direct Buried (DB) installations or exposed installations in non-hazardous Locations
			3. Heavy Wall (HW) for Encased Buried (EB) or Direct Buried (DB) installations where soil conditions require enhanced mechanical protection or exposed installations with enhanced mechanical protection in non-hazardous locations.
	2. REINFORCED THERMOSETTING RESIN FITTINGS-EPOXY
		1. Basis-of-Design Product: Subject to compliance with requirements, provide Atkore FRE® Composites (RTRC) fiberglass fittings.
		2. Fiberglass conduit fittings, elbows, and accessories shall be manufactured using the same filament winding process, methods, chemicals, and materials as the conduits and have a minimum socket depth and an inside bell design consistent with the conduit.
		3. Manufacturing process.
1. Fittings shall use the same filament winding process, methods, and components as used to manufacture the fiberglass conduit.
	* 1. All elbows comply with the nominal radius within plus or minus 3 degrees. Wall thicknesses complies with tolerances as indicated in the applicable standards below.
		2. All type SW, HW, XW HazGuard® conduits, elbows and fittings are durably and legibly marked in accordance UL Standards.as applicable. In addition, the following information shall be included in the marking:
			1. UL2515, UL2515A (For Type XW HazGuard® Only) & UL2420
			2. CSA C22.2 NO. 2515:19, CSA: C22.2 No. 2515.1-13 (For Type XW HazGuard® only) & CSA C22.2 No. 2420-09
			3. Manufacturer Listed
			4. Date of manufacturing of conduit, elbows, and fittings.
		3. Fittings, General: Listed and labeled for type of conduit, location, and use.
		4. Fittings for RTRC complies with UL 2420, UL 2515, or UL 2515A.
		5. Fittings for RTRC complies with CSA and manufactured in accordance with CSA C22.2 NO. 2515:19, CSA: C22.2 No. 2515.1-13 and CSA C22.2 No. 2420-09
		6. Adhesives: As recommended by conduit manufacturer.

# PART 3 – EXECUTION

# INSTALLATION

* + 1. Reinforced Thermosetting Resin Conduit, elbows and fittings shall be installed in compliance with the latest version of the National Electrical Code® (NEC®) and other applicable codes and standards as indicated elsewhere in these specifications.
		2. Reinforced Thermosetting Resin Conduit, elbows and fittings shall be installed in accordance with NECA National Electrical Installation Standard (NEIS) 111, *Standard for Installing Nonmetallic Raceways.*
		3. Reinforced Thermosetting Resin Conduit, elbows and fittings shall be installed in compliance with the latest version of the CSA C22.1:21 Canadian Electrical Code (CEC), Part I, Safety Standard for Electrical Installations.
		4. Reinforced Thermosetting Resin Conduit manufacturer will provide field certified installation training onsite. The manufacturer will provide training ensuring installation in accordance with manufacturers specifications and warranties.
		5. Upon completion of certified installation training, contractors will receive certificate of completion and provide as requested by owner.
		6. RTRC type SW & HW conduit shall be acceptable in non-hazardous locations as defined by National Electrical Code® (NEC®) and Canadian Electrical Code (CEC).
		7. RTRC type XW HazGuard® conduit is acceptable in areas subject to Physical Damage Locations Class 1 Division 2 per NFPA 70 NEC Section 501.10(B) Class 1 Division 2(1)(6). Also listed to UL 2515A/ CSA: C22.2 No. 2515.1-13.

 END OF SECTION