**Atkore – Allied Tube & Conduit**

This product specification is written according to the Construction Specifications Institute

*MasterFormat*, 2018 Update.

**SECTION 26 05 33.13**

**CONDUIT FOR ELECTRICAL SYSTEMS – Steel Electrical Metallic Tubing (EMT)**

# PART 1 - GENERAL

* 1. RELATED DOCUMENTS
     1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections apply to this Section.

# SUMMARY

* + 1. This Section includes the following:
       1. Steel Electrical Metallic Tubing (EMT)
    2. Related Sections
       1. Section 26 05 26 “Grounding and Bonding for Electrical Systems”
       2. Section 26 05 29 “Hangers and Supports for Electrical Systems”
       3. Section 26 05 33.16 “Boxes for Electrical Systems”
       4. Section 27 05 33 “Conduits and Backboxes for Communications Systems”
       5. Section 25 05 28.33 “Conduits and Backboxes for Integrated Automation”

# REFERENCES

* + 1. UL 797– Standard for Electrical Metallic Tubing– Steel
    2. ANSI C80.3– American National Standard for Steel Electrical Metallic Tubing (EMT)
    3. UL 514B – Standard for Conduit, Tubing and Cable Fittings
    4. NFPA 70 – National Electrical Code® (NEC®)
    5. NECA NEIS 101 – National Electrical Installation Standard for Installing Steel Conduits

# SUBMITTALS

* + 1. Product Data
    2. Certifications to applicable standards
    3. Domestic certifications: When required to Buy American Act or Buy America Act

# QUALITY ASSURANCE

* + 1. Electrical Metallic Tubing shall be listed to UL 797 and manufactured in accordance with ANSI C80.3.
    2. Electrical equipment and materials shall be new and within one year of manufacture, complying with the latest codes and standards. No used, re-built, refurbished and/or re- manufactured electrical equipment and materials shall be furnished on this project.
    3. Testing Agency Qualifications: An independent agency, with the experience and capability to conduct the testing indicated, that is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7 and that is acceptable to authorities having jurisdiction.

# DELIVERY, STORAGE AND HANDLING

* + 1. Delivery: Deliver products to site per the requirements of Section 01 65 00.
    2. Storage: If possible, store the conduit indoors to prevent possible discoloration, the accumulation of dirt and to extend the life of the product. However, if conduit is stored outdoors, it should be stored in such a way as to allow air circulation (do not cover directly with plastic, for example) and to allow water drain-off.

# PART 2 – PRODUCTS

* 1. MANUFACTURERS
     1. Atkore Allied Tube & Conduit,

16100 S Lathrop Ave.

Harvey, IL 60426; 1-800-882-5543

# STEEL ELECTRICAL METALLIC TUBING

* + 1. Electrical Metallic Tubing Steel shall be hot galvanized steel O.D. with an organic corrosion resistant I.D. coating in trade sizes ½ -4”.
    2. Electrical Metallic Tubing Steel shall be listed and manufactured in accordance with UL Safety Standard 797 and ANSI C80.3
    3. Product shall be labeled or marked showing evidence of third-party listing to product standard.
    4. Kwik-Fit® EMT and Compression EMT are tested to meet UL Safety Standard 514-B.

# FITTINGS

* + 1. Fittings shall be listed to UL 514B.

# ELBOWS

* + 1. Elbows shall be listed to UL 797 and manufactured in accordance with ANSI C80.3.

# PART 3 – EXECUTION

3.1 INSTALLATION

1. Electrical Metallic Tubing Steel shall be installed in compliance with the latest version of the National Electrical Code and other applicable codes and standards as indicated elsewhere in these specifications.
2. Electrical Metallic Tubing Steel shall be installed in accordance with NECA National Electrical Installation Standard (NEIS) 101, *Standard for Installing Steel Conduits.*

END OF SECTION