## P-C_P-Ssubmittal data
Condo Pack A2L Submittal Sheet Data: P-C & P-S
| Cooling Performance |  |  |  | Heating Performance |  |  |  | Supply Air Blower Performance |  |  | Electrical Data |  |  | Unit Details
CP A2L Models | Capacity (BTU/h) | Efficiency Type (Variable, EER or SEER) | Efficeincy Value (Variable, specific to model) | Refrigerant | Input Capacity (BTU/h) | Output Capacity (BTU/h) | AFUE/ TE | Air Temp Rise (°F) | Maximum Factory Supply Air (CFM) | External Static Pressure (In.W.C.) | Motor Rating (HP) | Power Supply | MCA = Minimum Circuit Ampacity (A) | MOP = Maximum Overload Protective Device (A) | Unit Shipping Weight (lbs.) | Cabinet Size***
P-C: Condensing Gas Heat Condo Packs
P-C15A1-B12A-A | 12300 | SEER2 | 11.7 | R454B | 15000 | 14500 | 96.8 | 25-35 | 449/341 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 11.3 | 15 | 328 | 43 1/8” High x 28” Wide x 32” Deep
P-C30A1-B12A-A | 12300 | SEER2 | 11.7 | R454B | 30000 | 28000 | 93 | 35-65 | 449/341 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 11.3 | 15 | 328 | 43 1/8” High x 28” Wide x 32” Deep
P-C30A1-B18A-A | 17000 | SEER2 | 11.7 | R454B | 30000 | 28000 | 93 | 35-65 | 641/551 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 14.9 | 20 | 349
P-C30A1-B24A-A | 21200 | SEER2 | 11.7 | R454B | 30000 | 28000 | 93 | 35-65 | 806/728 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 17.1 | 25 | 349
P-C40A1-B18A-A | 17000 | SEER2 | 11.7 | R454B | 40000 | 37000 | 91.7 | 35-65 | 641/551 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 14.9 | 20 | 349 | 43 1/8” High x 28” Wide x 32” Deep
P-C40A1-B24A-A | 21200 | SEER2 | 11.7 | R454B | 40000 | 37000 | 91.7 | 35-65 | 806/728 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 17.1 | 25 | 349
P-C40A2-B30A-A | 26400 | SEER2 | 11.7 | R454B | 40000 | 37000 | 91.7 | 35-65 | 932/867 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 23.6 | 35 | 366
P-C50A1-B18A-A | 17000 | SEER2 | 11.7 | R454B | 50000 | 45300 | 90.6 | 35-65 | 881/784 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 14.9 | 20 | 349 | 43 1/8” High x 28” Wide x 32” Deep
P-C50A1-B24A-A | 21200 | SEER2 | 11.7 | R454B | 50000 | 45300 | 90.6 | 35-65 | 881/784 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 17.1 | 25 | 349
P-C50A2-B30A-A | 26400 | SEER2 | 11.7 | R454B | 50000 | 45300 | 90.6 | 35-65 | 932/867 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 23.6 | 35 | 366
P-S: Non-Condensing Gas Heat Condo Packs
P-S26A1-B12A-A | 12300 | SEER2 | 11.7 | R454B | 26000 | 21000 | 80 | 27-35 | 449/341 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 11.3 | 15 | 328 | 43 1/8” High x 28” Wide x 32” Deep
P-S26A1-B18A-A | 17000 | SEER2 | 11.7 | R454B | 26000 | 21000 | 80 | 27-35 | 641/551 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 14.9 | 20 | 349
P-S38A1-B12A-A | 12300 | SEER2 | 11.7 | R454B | 38000 | 30400 | 80 | 35-65 | 454/313 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 11.3 | 15 | 328 | 43 1/8” High x 28” Wide x 32” Deep
P-S38A1-B18A-A | 17000 | SEER2 | 11.7 | R454B | 38000 | 30400 | 80 | 35-65 | 641/551 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 14.9 | 20 | 349
P-S38A1-B24A-A | 21200 | SEER2 | 11.7 | R454B | 38000 | 30400 | 80 | 35-65 | 806/728 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 17.1 | 25 | 349
P-S51A1-B18A-A | 17000 | SEER2 | 11.7 | R454B | 51000 | 41000 | 80 | 40-60 | 678/576 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 14.9 | 20 | 349 | 43 1/8” High x 28” Wide x 32” Deep
P-S51A1-B24A-A | 21200 | SEER2 | 11.7 | R454B | 51000 | 41000 | 80 | 40-60 | 806/728 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 17.1 | 25 | 349
P-S51A2-B30A-A | 26400 | SEER2 | 11.7 | R454B | 51000 | 41000 | 80 | 40-60 | 932/867 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 23.6 | 35 | 366
P-S64B1-B18A-A | 17000 | SEER2 | 11.7 | R454B | 64000 | 51200 | 80 | 35-65 | 901/818 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 14.9 | 20 | 349 | 43 1/8” High x 28” Wide x 32” Deep
P-S64B1-B24A-A | 21200 | SEER2 | 11.7 | R454B | 64000 | 51200 | 80 | 35-65 | 901/818 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 17.1 | 25 | 349
P-S64B2-B30A-A | 26400 | SEER2 | 11.7 | R454B | 64000 | 51200 | 80 | 35-65 | 932/867 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 23.6 | 35 | 366
*** This data is only for salisfy,not needed on webiste submittals sheet.

## P-E_submittal data
Condo Pack A2L Submittal Sheet Data: P-E
| Cooling Performance |  |  |  | Heating Performance |  |  |  | Supply Air Blower Performance |  |  | Electrical Data |  |  |  |  | Unit Details
CP A2L Models | Capacity (BTU/h) | Efficiency Type (Variable, EER or SEER) | Efficeincy Value (Variable, specific to model) | Refrigerant | Heating Capacity at 240V (kW) | Heating Capacity at 208V (kW) | Air Temperature Rise at 240V (°F) | Air Temperature Rise at 208V (°F) | Maximum Factory Supply Air (CFM) | External Static Pressure (In.W.C.) | Motor Rating (HP) | Power Supply | MCA = Minimum Circuit Ampacity (A) at 240V | MCA = Minimum Circuit Ampacity (A) at 208V | MOP = Maximum Overload Protective Device (A) at 240V | MOP = Maximum Overload Protective Device (A) at 208V | Unit Shipping Weight (lbs.) | Cabinet Size***
P-E: Electric Heat Condo Packs
P-E05B1-B12A-A | 12300 | SEER2 | 11.7 | R454B | 4.8 | 3.6 | 38 | 33 | 449/341 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 30 | 26.6 | 30 | 30 | 321 | 43 1/8” High x 28” Wide x 32” Deep
P-E05B1-B18A-A | 17000 | SEER2 | 11.7 | R454B | 4.8 | 3.6 | 38 | 33 | 641/551 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 30 | 26.6 | 30 | 30 | 331
P-E07B1-B12A-A | 12300 | SEER2 | 11.7 | R454B | 7.3 | 5.5 | 45 | 37 | 449/341 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 43 | 38 | 45 | 40 | 322 | 43 1/8” High x 28” Wide x 32” Deep
P-E07B1-B18A-A | 17000 | SEER2 | 11.7 | R454B | 7.3 | 5.5 | 45 | 37 | 641/551 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 43 | 38 | 45 | 40 | 332
P-E07B1-B24A-A | 21200 | SEER2 | 11.7 | R454B | 7.3 | 5.5 | 45 | 37 | 806/728 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 43 | 38 | 45 | 40 | 332
P-E10B1-B18A-A | 17000 | SEER2 | 11.7 | R454B | 9.6 | 7.2 | 56 | 45 | 641/551 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 55 | 48.3 | 60 | 50 | 333 | 43 1/8” High x 28” Wide x 32” Deep
P-E10B1-B24A-A | 21200 | SEER2 | 11.7 | R454B | 9.6 | 7.2 | 56 | 45 | 806/728 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 55 | 48.3 | 60 | 50 | 333
P-E10B2-B30A-A | 26400 | SEER2 | 11.7 | R454B | 9.6 | 7.2 | 56 | 45 | 932/867 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 55 | 48.3 | 60 | 50 | 350
P-E15B1-B24A-A | 21200 | SEER2 | 11.7 | R454B | 14.4 | 10.8 | 55 | 44 | 806/728 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 80 | 69.9 | 80 | 70 | 334 | 43 1/8” High x 28” Wide x 32” Deep
P-E15B2-B30A-A | 26400 | SEER2 | 11.7 | R454B | 14.4 | 10.8 | 55 | 44 | 932/867 | 0.2/0.5 | 1/2HP | 208/230V-60Hz-1PH | 80 | 69.9 | 80 | 70 | 351
*** This data is only for salisfy,not needed on webiste submittals sheet.